## Storage Tank Heater
Storage Tank Water Heater Sizing Calculator
Developed by the Plan Review Unit of the Environmental Health Section NC Division of Public Health
Establishment Name: |  | fghd
Address: |  | sdfgsdfg
EQUIPMENT | [7 empty] | GPH CALCULATED
Enter the description, and number and size of compartments for each sink |  | Description | Number of compartments |  |  | (Inches) |  | Gallons Per Hour (GPH)
[5 empty] | Length | Width | Depth
Manual warewashing sink | [7 empty] | 0
Sink #2 | [7 empty] | 0
Sink #3 | [7 empty] | 0
Bar sink | [7 empty] | 0
Sinks are calculated at 75% capacity | [6 empty] | Total | 0
Enter type of prep sink and number of sink compartments for each sink |  | Type of prep sink (vegetable, meat, seafood) |  | Number of compartments |  |  |  | Gallons Per Hour (GPH)
Prep sink #1 | [7 empty] | 0
Prep sink #2 | [7 empty] | 0
Prep sink #3 | [7 empty] | 0
Prep sinks are calculated at 5 gallons per compartment | [6 empty] | Total | 0
Enter the quantity of equipment |  | Quantity | [5 empty] | Gallons Per Hour (GPH)
Handwashing sinks | [7 empty] | 0
Service sink | [7 empty] | 0
Hose reel | [7 empty] | 0
Clothes washer | [7 empty] | 0
Enter a description and estimated gallon per hour (GPH) usage for other equipment |  | Description |  | Estimated gallons per hour (GPH) usage
Other equipment | [7 empty] | 0
Other equipment | [7 empty] | 0
Other equipment | [7 empty] | 0
Handwashing sinks and service sinks are calculated at 5 GPH each. | [6 empty] | Total | 0
Hose reels are calculated at 5 GPH, clothes washers at 15 GPH, other equipment at the usage entered.
Enter make, model, and Final Rinse Usage gallons per hour (GPH) for the warewashing machine |  | Make | Model | Final Rinse Usage (GPH) Found in "Warewashing Machine Specs" tab below or on manufacturer's spec sheet |  |  |  | Gallons Per Hour (GPH)
Warewashing machine | [7 empty] | 0
Enter the quantity of pre-rinse units |  | Quantity | [5 empty] | Gallons Per Hour (GPH)
Pre-rinse | [7 empty] | 0
Warewashing machines are calculated at 70% of the final rinse usage specified by the manufacturer. | [6 empty] | Total | 0
Pre-rinses are calculated at 45 GPH.
Recovery Rate Needed (GPH): | [7 empty] | 0
Water Heater Input (BTU or kW) Needed:
|  | Gas Water Heater |  | Electric Water Heater
| 0 | ,000 BTU at 70ºF | rise | 0 | kW at 70ºF rise
| 0 | ,000 BTU at 80°F rise |  | 0 | kW at 80°F rise
| 0 | ,000 BTU at 90°F rise |  | 0 | kW at 90°F rise
| 0 | ,000 BTU at 100°F rise |  | 0 | kW at 100°F rise

## Tankless Heater
Tankless Water Heater Sizing Calculator
Developed by the Plan Review Unit of the Environmental Health Section NC Division of Public Health
Enter the quantity of each piece of equipment listed below.
For other equipment enter the description and gallon per minute (GPM) value.
Find dishmachine GPM on the "Dishmachine Specs" sheet below or on the manufacturer's spec sheet
Establishment Name:
Address:
Equipment | Quantity |  | GPM Calculated
Handwashing sink |  | .5 GPM each | 0
Warewashing sink |  | 2 GPM each | 0
Prep sink |  | 1 GPM each | 0
Service sink |  | 1 GPM each | 0
Other equipment | Description | GPM value
Other equipment |  |  | 0
Other equipment |  |  | 0
Other equipment |  |  | 0
Dishmachine Brand | Dishmachine Model | Dishmachine GPM
0
Pre-rinse Quantity |  | 2 GPM each | 0
Total Gallons per Minute (GPM) Needed: |  |  | 0

## Dishmachine Specs
| Model Number | Conveyor | Flow | Usage | (Max.)
| Number | Width | gpm | gph | (ft/min.)
ADAMATION, INC.
CONVEYOR DISHWASHING MACHINES
| Model | Conveyor | Flow | Usage | (Max.)
| Number | Width | gpm | gph | (ft/min.)
Single Tank Rack Conveyor
| CA-1 | 20x20 | 3.01 | 180.6 | 8.2
Multiple Tank Rack Conveyor
| CSL-1390 | 20x20 | 4.9 | 294 | 10
| CA-2 | 20x20 | 4.3 | 258 | 14.3
| CA-3 | 20x20 | 4.3 | 258 | 14.3
| CA-3SR | 20x20 | 4.3 | 258 | 14.3
| CA-3SW | 20x20 | 4.3 | 258 | 14.3
| CA-4 | 20x20 | 1.87 | 112 | 21.5
| CA-4SR | 20x20 | 1.87 | 112 | 21.5
| CA-4SW | 20x20 | 1.87 | 112 | 21.5
| CA-4SW/SR | 20x20 | 1.87 | 112 | 21.5
| SLAP44-XX-XX | 20x20 | 1.91 | 115 | 6.8
ALVEY WASHING EQUIPMENT COMPANY
CONVEYOR POT, PAN, AND UTENSIL WASHING MACHINES
| Model | Conveyor | Flow | Usage | (Max.)
| Number | Width | gpm | gph | (ft/min.)
Multiple Tank Conveyor - Hot Water Sanitizing
| C2TW9984 | 30 | 9.39 | 563 | 5
Single Tank Conveyor - Hot Water Sanitizing
| C1TW3020 | 32 | 4 | 242 | 18.75
| KS-88-C | 36 | 2.84 | 170 | 5.51
| TT-84 | 27 | 9.6 | 574 | 2.4
STATIONARY RACK POT, PAN, AND UTENSIL WASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
Single Tank Moving Rack - Hot Water Sanitizing
| TT-74-N | 0x0 | 17.0 | 289 | 120 | 60
Single Tank Stationary Rack - Hot Water Sanitizing
| CL-1 | 35x25 | 9 | 99 | 120 | 30
| FL-2S | 36x30 | 9.5 | 81 | 142 | 30
| FLC-10 | 27x26 | 6.6 | 66 | 120 | 30
| FLC-36 | 34x72 | 10.2 | 122.4 | 180 | 60
| KS-48 | 61x36 | 9.4 | 109 | 180 | 60
| KS-70-N | 69x49 | 23.5 | 446 | 120 | 60
| KS-88-N | 69x65 | 23.5 | 446 | 120 | 60
| SA-5A | 35x25 | 8.3 | 95.7 | 120 | 30
| SL-2D | 27x26 | 13.2 | 145 | 120 | 30
| SL-2S | 27x26 | 6.6 | 76 | 120 | 30
| SMT-88 | 69x65 | 23.5 | 446 | 120 | 60
AMERICAN DISH SERVICE
CONVEYOR DISHWASHING MACHINES
| Model | Conveyor | Flow | Usage | (Max.)
| Number | Width | gpm | gph | (ft/min.)
Multiple Tank Rack Conveyor Dishwasher - Chemical Sanitizing
| ADC-44 | 20" | 2.0 | 120 | 6.8
| ADC-66 | 20" | 2.0 | 120 | 6.8
Multiple Tank Rack Conveyor Dishwasher - Hot Water Sanitizing
| ADC-44 | 20" | 2.0 | 120 | 6.8
| ADC-66 | 20" | 2.0 | 120 | 6.8
STATIONARY RACK DISHWASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
Single Tank Stationary Rack Chemical Sanitizing
| A-3D | 20x20 | N/A | 61.6 | 60 | 45
| A-3D-S | 20x20 | N/A | 61.6 | 60 | 45
| A | 20x20 | N/A | 61.6 | 60 | 45
| A-B | 20x20 | N/A | 70 | 60 | 45
| AC | 20x20 | N/A | 61.6 | 60 | 45
| AC-3D | 20x20 | N/A | 61.6 | 60 | 45
| AC-3D-S | 20x20 | N/A | 61.6 | 60 | 45
| AD-25 | 20x20 | N/A | 71 | 45 | 30
| AF | 20x20 | N/A | 81.4 | 45 | 30
| AF-3D | 20x20 | N/A | 81.4 | 45 | 30
| AF-3D-S | 20x20 | N/A | 81.4 | 45 | 30
| AF-B | 20x20 | N/A | 92.5 | 45 | 30
| AFC | 20x20 | N/A | 81.4 | 45 | 30
| AFC-3D | 20x20 | N/A | 81.4 | 45 | 30
| AFC-3D-S | 20x20 | N/A | 81.4 | 45 | 30
| AFW | 20x20 | N/A | 81.4 | 45 | 30
| AFWC | 20x20 | N/A | 81.4 | 45 | 30
| AH | 20x20 | N/A | 50.6 | 75 | 60
| AH-3D | 20x20 | N/A | 50.6 | 75 | 60
| AH-3D-S | 20x20 | N/A | 50.6 | 75 | 60
| AH-B | 20x20 | N/A | 57.5 | 75 | 60
| AHC | 20x20 | N/A | 50.6 | 75 | 60
| AHC-3D | 20x20 | N/A | 50.6 | 75 | 60
| AHC-3D-S | 20x20 | N/A | 50.6 | 75 | 60
| ET-A | 20x20 | N/A | 40.8 | 60 | 45
| ET-AF | 20x20 | N/A | 51 | 45 | 30
| ET-AF-3 | 20x20 | N/A | 60 | 45 | 30
| ET-AF-M | 20x20 | N/A | 60 | 45 | 30
| ET-AH | 20x20 | N/A | 34 | 75 | 60
| ET-A-M | 20x20 | N/A | 48 | 60 | 45
| ET-AH-M | 20x20 | N/A | 40 | 75 | 60
| ET-A-3 | 20x20 | N/A | 48 | 60 | 45
| ET-AH-3 | 20x20 | N/A | 40 | 75 | 60
| HT-25 | 20x20 | N/A | 58.65 | 35 | 10
| L-60-3D | 20x20 | N/A | 66 | 36 | 15
| L-60-3D-K | 20x20 | N/A | 66 | 36 | 15
| L-60-3DC | 20x20 | N/A | 66 | 36 | 15
| L-60-3DC-K | 20x20 | N/A | 66 | 36 | 15
| L-60-3DW | 20x20 | N/A | 66 | 36 | 15
| L-60-3DW-K | 20x20 | N/A | 66 | 36 | 15
| L-60-3DWC | 20x20 | N/A | 66 | 36 | 15
| L-60-3DWC-K | 20x20 | N/A | 66 | 36 | 15
| L-72-3D | 20x20 | N/A | 55 | 43 | 19
| L-72-3D-K | 20x20 | N/A | 55 | 43 | 19
| L-72-3DC | 20x20 | N/A | 55 | 43 | 19
| L-72-3DC-K | 20x20 | N/A | 55 | 43 | 19
| L-72-3DW | 20x20 | N/A | 55 | 43 | 19
| L-72-3DW-K | 20x20 | N/A | 55 | 43 | 19
| L-72-3DWC | 20x20 | N/A | 55 | 43 | 19
| L-72-3DWC-K | 20x20 | N/A | 55 | 43 | 19
| L-90-3D | 20x20 | N/A | 44 | 50 | 30
| L-90-3D-K | 20x20 | N/A | 44 | 50 | 30
| L-90-3DC | 20x20 | N/A | 44 | 50 | 30
| L-90-3DC-K | 20x20 | N/A | 44 | 50 | 30
| L-90-3DW | 20x20 | N/A | 44 | 50 | 30
| L-90-3DW-K | 20x20 | N/A | 44 | 50 | 30
| L-90-3DWC | 20x20 | N/A | 44 | 50 | 30
| L-90-3DWC-K | 20x20 | N/A | 44 | 50 | 30
| W | 20x20 | N/A | 61.6 | 60 | 45
| WC | 20x20 | N/A | 61.6 | 60 | 45
| WH | 20x20 | N/A | 50.6 | 75 | 60
| WHC | 20x20 | N/A | 50.6 | 75 | 60
| SS-25 | 20x20 | N/A | 71 | 45 | 30
Double Tank Stationary Rack Chemical Sanitizing
| 5 | 2*20x20 | N/A | 89.6 | 60 | 45
| 5-S | 2*20x20 | N/A | 89.6 | 60 | 45
| 5-AG | 2*20x20 | N/A | 118.4 | 45 | 30
| 5-AGS | 2*20x20 | N/A | 118.4 | 45 | 30
| 5-AH | 2*20x20 | N/A | 73.6 | 75 | 60
| 5-AHS | 2*20x20 | N/A | 73.6 | 75 | 60
Single Tank Stationary Rack Hot Water Sanitizing
| HT-25 | 20x20 | N/A | 61.2 | 35 | 10
AUTO-CHLOR SYSTEM, INC.
STATIONARY RACK DISHWASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
Single Tank Door Chemical Sanitizing
| A4 | 20x20 | N/A | 43.7 | 56 | 24
| A5 | 20x20 | N/A | 43.7 | 56 | 24
| A4IW | 20x20 | N/A | 43.7 | 56 | 24
| A5IW | 20x20 | N/A | 43.7 | 56 | 24
| M4 | 20x20 | N/A | 43.7 | 56 | 24
| U38 | 20x20 | N/A | 43.7 | 56 | 24
| U34 | 20x20 | N/A | 43.7 | 56 | 24
Single Tank Door Double Rack Chemical Sanitizing
| D2 | 2*20x20 | N/A | 118 | 56 | 32
| D2CL | 2*20x20 | N/A | 118 | 56 | 32
| D2CR | 2*20x20 | N/A | 118 | 56 | 32
AUTO-CHLOR SYSTEM, INC.
CONVEYOR DISHWASHING MACHINES
| Model | Conveyor | Flow | Usage | (Max.)
| Number | Width | gpm | gph | (ft/min.)
Multiple Tank Rack Conveyor Dishwasher - Chemical Sanitizing
| AC-44 | 20" | 2 | 120 | 6.8
| AC-44-RC | 20" | 2 | 120 | 6.8
| AC-66 | 20" | 2 | 120 | 6.8
Multiple Tank Rack Conveyor Dishwasher - Hot Water Sanitizing
| AC-44 | 20" | 2 | 120 | 6.8
| AC-44-RC | 20" | 2 | 120 | 6.8
| AC-66 | 20" | 2 | 120 | 6.8
BLAKESLEE
CONVEYOR DISHWASHING MACHINES
| Model | Conveyor | Flow | Usage | (Max.)
| Number | Width | gpm | gph | (ft/min.)
Multiple Tank Rack Conveyor, Hot Water Sanitizing
| R-CC64 | 20x20 | 4.5 | 270 | 5.6
| R-PCC | 20x20 | 4.5 | 270 | 5.6
| R-EE | 20x20 | 4.5 | 270 | 5.6
| R-PEE | 20x20 | 4.5 | 270 | 5.6
| R-LL | 20x20 | 4.5 | 270 | 5.6
| R-PLL | 20x20 | 4.5 | 270 | 5.6
| R-MM | 20x20 | 4.5 | 270 | 5.6
| R-PMM | 20x20 | 4.5 | 270 | 5.6
| R-EEE | 20x20 | 4.5 | 270 | 5.6
| R-LLL | 20x20 | 4.5 | 270 | 5.6
| R-MMM | 20x20 | 4.5 | 270 | 5.6
Multiple Tank Flight Conveyor, Hot Water Sanitizing
| F-EE | 20 | 4.8 | 288 | 6.6
| FA-EE | 20 | 4.8 | 288 | 6.6
| F-PEE | 20 | 4.8 | 288 | 6.6
| FA-PEE | 20 | 4.8 | 288 | 6.6
| F-LL | 20 | 4.8 | 288 | 8.2
| FA-LL | 20 | 4.8 | 288 | 8.2
| F-PLL | 20 | 4.8 | 288 | 8.2
| FA-PLL | 20 | 4.8 | 288 | 8.2
| F-MM | 20 | 4.8 | 288 | 8.2
| FA-MM | 20 | 4.8 | 288 | 8.2
| F-PMM | 20 | 4.8 | 288 | 8.2
| FA-PMM | 20 | 4.8 | 288 | 8.2
| F-EEE | 20 | 4.8 | 288 | 8.2
| FA-EEE | 20 | 4.8 | 288 | 8.2
| F-LLL | 20 | 4.8 | 288 | 8.2
| FA-LLL | 20 | 4.8 | 288 | 8.2
| F-MMM | 20 | 4.8 | 288 | 8.2
| FA-MMM | 20 | 4.8 | 288 | 8.2
| XF-EE | 30 | 2.76 | 166 | 9.1
| XF-PEE | 30 | 2.76 | 166 | 9.1
| XF-LL | 30 | 2.76 | 166 | 9.1
| XF-PLL | 30 | 2.76 | 166 | 9.1
| XF-MM | 30 | 2.76 | 166 | 9.1
| XF-PMM | 30 | 2.76 | 166 | 9.1
| XF-EEE | 30 | 2.76 | 166 | 9.1
| XF-LLL | 30 | 2.76 | 166 | 9.1
| XF-MMM | 30 | 2.76 | 166 | 9.1
Single Tank Rack Conveyors, Hot Water Sanitizing
| R-M | 20x20 | 5 | 300 | 5.5
| R-E | 20x20 | 7 | 420 | 5
| R-PE | 20x20 | 7 | 420 | 5
| R-L | 20x20 | 5 | 300 | 5.5
| R-PL | 20x20 | 5 | 300 | 5.5
| R-PM | 20x20 | 5 | 300 | 5.5
Single Tank Flight Conveyor, Hot Water Sanitizing
| F-E | 20 | 4.7 | 282 | 4.6
| F-PE | 20 | 4.7 | 282 | 4.6
| F-L | 20 | 4.7 | 282 | 4.6
| F-PL | 20 | 4.7 | 282 | 4.6
| F-M | 20 | 4.7 | 282 | 4.6
| F-PM | 20 | 4.7 | 282 | 4.6
Multiple Tank Flight Conveyor, Chemical Sanitizing
| XF-EE-LT | 30 | 2.8 | 166 | 9
| XF-PEE-LT | 30 | 2.8 | 166 | 9
| XF-LL-LT | 30 | 2.8 | 166 | 9
| XF-PLL-LT | 30 | 2.8 | 166 | 9
| XF-MM-LT | 30 | 2.8 | 166 | 9
| XF-PMM-LT | 30 | 2.8 | 166 | 9
| XF-EEE-LT | 30 | 2.8 | 166 | 9
| XF-LLL-LT | 30 | 2.8 | 166 | 9
| XF-MMM-LT | 30 | 2.8 | 166 | 9
Multiple Tank Rack Conveyor, Chemical Sanitizing
| R-CC64-LT | 20x20 | 2.2 | 134 | 7
| R-PCC-LT | 20x20 | 2.2 | 134 | 7
| R-EE-LT | 20x20 | 2.2 | 134 | 7
| R-PEE-LT | 20x20 | 2.2 | 134 | 7
| R-LL-LT | 20x20 | 2.2 | 134 | 7
| R-PLL-LT | 20x20 | 2.2 | 134 | 7
| R-MM-LT | 20x20 | 2.2 | 134 | 7
| R-PMM-LT | 20x20 | 2.2 | 134 | 7
| R-EEE-LT | 20x20 | 2.2 | 134 | 7
| R-LLL-LT | 20x20 | 2.2 | 134 | 7
| R-MMM-LT | 20x20 | 2.2 | 134 | 7
STATIONARY RACK DISHWASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
Single Tank Stationary Rack Chemical Sanitizing Door
| D-9 | 20x20 | 31.5 | 96.2 | 46 | 29
Single Tank Stationary Rack Door, Hot Water Sanitizing
| D-8 | 20x20 | 1.3 | 72 | 49 | 11
Undercounter Dishmachines, Hot Water Sanitizing
| UC-21A | 20x20 | 4.3 | 21.6 | 105 | 10
| UC-21B | 20x20 | 4.3 | 21.6 | 105 | 10
CENTPAR INDUSTRIES
STATIONARY RACK POT, PAN, AND UTENSIL WASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
Single Tank Stationary Rack - Hot Water Sanitizing[2]
| PW-36 | 28x28 | 12.7 | 80.3 | 120 | 20
| PW-36C | 28x28 | 12.7 | 80.3 | 120 | 20
| PW-36PT | 28x28 | 12.7 | 80.3 | 120 | 20
| PW-36TD | 28x28 | 12.7 | 80.3 | 120 | 20
Single Tank Moving Rack - Hot Water Sanitizing[1] [2]
| PW-48 | NA | 14.1 | 108.5 | 120 | 25
| PW-48C | NA | 14.1 | 108.5 | 120 | 25
| PW-48TD | NA | 14.1 | 108.5 | 120 | 25
CHAMPION INDUSTRIES, INC.
CONVEYOR DISHWASHING MACHINES
| Model | Conveyor | Flow | Usage | (Max.)
| Number | Width | gpm | gph | (ft/min.)
Multiple Tank Rack Conveyor - Chemical Sanitizing
| K-L66 | 20x20 | 4.26 | 256 | 5
Multiple Tank Rack Conveyor - Hot Water Sanitizing
| 40-KB | 20x20 | 5 | 300 | 7.6
| 40-KB-2-2 | 20x20 | 5 | 300 | 7.6
| 40-KFWB | 20x20 | 5 | 300 | 7.6
| 40-KPRB | 20x20 | 5 | 300 | 7.6
| 40-KPRB-2-2 | 20x20 | 5 | 300 | 7.6
| 40-KPRB-2-3 | 20x20 | 5 | 300 | 7.6
| 60-KB | 20x20 | 5 | 300 | 9.2
| 60-KB-2-2 | 20x20 | 5 | 300 | 9.2
| 60-KFWB | 20x20 | 5 | 300 | 9.2
| 60-KFWB-2-2 | 20x20 | 5 | 300 | 9.2
| 60-KPRB | 20x20 | 5 | 300 | 9.2
| 60-KPRB-2-3 | 20x20 | 5 | 300 | 9.2
| 64 | 20x20 | 4 | 241 | 7.7
| 64-KB | 20x20 | 5 | 300 | 7
| 64-KB Corner | 20x20 | 5 | 300 | 7
| 64-KPRB | 20x20 | 5 | 300 | 7
| 64-KPRB Corner | 20x20 | 5 | 300 | 7
| 86 PW | 20x20 | 4 | 241 | 7.7
| USN72-135 | 20x20 | 4.75 | 285 | 3.5
| USN72-185 | 20x20 | 4.75 | 285 | 5.1
| USN72-250 | 20x20 | 4.75 | 285 | 7
| USN72-60 | 20x20 | 4.75 | 285 | 1.7
| USN72-85 | 20x20 | 4.75 | 285 | 2.4
Multiple Tank Rackless Conveyor - Hot Water Sanitizing [8]
| UC**CW Series 6ft. Center | 29 | 7.1 | 426 | 6.5
| UC**CW Series 8ft. Center | 29 | 7.1 | 426 | 9.5
| UC**Series 6 ft. Center | 24 | 5.6 | 336 | 6.5
| UC**Series 8 ft. Center | 24 | 5.6 | 336 | 9.5
| UC-CW6-WS | 29 | 3.17 | 190 | 7.9
| UC-CW8-WS | 29 | 3.75 | 225 | 11
| W-6 | 58 | 14.2 | 852 | 9.5
| W-6-WS | 58 | 7.7 | 460 | 10.9
Single Tank Rack Conveyor - Chemical Sanitizing
| K-L44 | 20x20 | 4.26 | 256 | 5
Single Tank Rack Conveyor - Hot Water Sanitizing
| 44 | 20x20 | 3.89 | 233 | 5.8
| 44 WS | 20x20 | 2 | 124 | 3.5
| 44-KB | 20x20 | 5.4 | 324 | 5.6
| 44-KB Corner | 20x20 | 5.4 | 324 | 5.6
| 44-KPRB | 20x20 | 5.4 | 324 | 5.6
| 44-KPRB Corner | 20x20 | 5.4 | 324 | 5.6
| 44-WS | 20x20 | 2.17 | 130 | 3.4
| 54-KB | 20x20 | 5.4 | 324 | 5.6
| 54-KB Corner | 20x20 | 5.4 | 324 | 5.6
| 54-KPRB | 20x20 | 5.4 | 324 | 5.6
| 54-KPRB Corner | 20x20 | 5.4 | 324 | 5.6
| 66 PW | 20x20 | 3.89 | 233 | 5.8
| 66 WSPW | 20x20 | 2 | 124 | 3.5
| 66-WS | 20x20 | 2.17 | 130 | 3.4
Single Tank Rackless Conveyor - Hot Water Sanitizing [8]
| UC-C4 | 24 | 5.6 | 336 | 6.9
| UC-CW4 | 29 | 6 | 362 | 8
STATIONARY RACK DISHWASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
Single Tank Door - Chemical Sanitizing
| D-LF | 20x20 | 5.2 | 66 | 45 | 14
| U-LD | 20x20 | 56 | 44 | 62 | 32
| UL-100 | 20x20 | 9.2 | 44 | 80 | 15
Single Tank Door - Hot Water Sanitizing
| D-H1 | 20x20 | 6.6 | 61 | 40 | 10
| D-H1T | 20x20 | 6.2 | 65.7 | 44 | 13
| D-HB | 20x20 | 6.6 | 61 | 40 | 10
| D-HBT | 20x20 | 6.2 | 65.7 | 44 | 13
| U-H1 | 20x20 | 3.2 | 33 | 67 | 21
| U-HB | 20x20 | 3.2 | 33 | 67 | 21
| UH-100 | 20x20 | N/A | 43 | 60 | 15
| UH-100B | 20x20 | N/A | 43 | 60 | 15
| UH-200 | 20x20 | 6.0 | 33 | 60 | 11
| UH-200B | 20x20 | 6.0 | 33 | 60 | 11
| USN10 | 16x16 | .6 | 36 | 33 | 12
STATIONARY RACK POT, PAN, AND UTENSIL WASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
Single Tank Stationary Rack - Hot Water Sanitizing
| D-H1T | 20x20 | 6.2 | 25.5 | 156 | 13
| D-HBT | 20x20 | 6.2 | 25.5 | 156 | 13
| PP-28 | 28x28 | 12.3 | 82.0 | 120 | 16
STATIONARY RACK DISHWASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
Single Tank Door, Hot Water
| DHB-VS | 20x20 | N/A | 48.4 | 43 | 10
Single Tank, Chemical Sanitizing Undercounter Dishwashing Machines
| UL-150 | 20x20 | 3.6 | 38 | 80 | 23
Stationary Rack Dishwashing Machines
| UH-150 | 20x20 | 4 | 42 | 80 | 23
| UH-150B | 20x20 | 4 | 42 | 80 | 23
CLASSIC GLASS & DISHWASHING SYSTEMS LTD
STATIONARY RACK DISHWASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
STATIONARY RACK DISHWASHING MACHINES
Single Tank Door
| H850S | 20x20 | 1.79 | 45.7 | 37 | 28
Single Tank Undercounter
| H500S | 16x16 | 2.53 | 14.2 | 107 | 14
| H750S | 20x20 | 3.92 | 23.5 | 105 | 15
| Eco-1 | 14x14 | 2.10 | 6.4 | 226 | 14
| H800S | 20x20 | 3.92 | 23.5 | 105 | 15
CMA DISHMACHINES
CONVEYOR DISHWASHING MACHINES
| Model | Conveyor | Flow | Usage | (Max.)
| Number | Width | gpm | gph | (ft/min.)
Multiple Tank Rack Conveyor, Hot Water Sanitizing
| CMA-44H | 20 | 3.2 | 192 | 5.7
| CMA-66H | 20 | 3.2 | 192 | 5.7
Multiple Tank Rack Conveyor, Chemical Sanitizing
| CMA-44L | 20 | 3.2 | 192 | 6.75
| CMA-66L | 20 | 3.2 | 192 | 6.75
STATIONARY RACK DISHWASHING MACHINES
Single Tank Stationary Rack, Chemical Sanitizing
| A-1 | 20x20 | 52 | 56 | 57 | 48
| A-2 | 20x20 | 52 | 74 | 45 | 30
| A-3 | 20x20 | 52 | 46 | 80 | 55
| AH-1 | 20x20 | 52 | 56 | 57 | 48
| AH-2 | 20x20 | 52 | 74 | 45 | 30
| AH-3 | 20x20 | 52 | 46 | 80 | 55
| C-1 | 20x20 | 52 | 56 | 57 | 48
| C-2 | 20x20 | 52 | 74 | 45 | 30
| C-3 | 20x20 | 52 | 46 | 80 | 55
| CMA-180 LTC | 20x20 |  | 50 | 49 | 12
| CMA-180 LTCB | 20x20 |  | 50 | 49 | 12
| CMA-180 LTS | 20x20 |  | 52 | 49 | 12
| CMA-180 LTSB | 20x20 |  | 52 | 49 | 12
| CVA-1 | 20x20 | 52 | 35 | 65 | 48
| CVA-2 | 20x20 | 52 | 46.2 | 53 | 30
| CVA-3 | 20x20 | 52 | 28.8 | 88 | 55
| CVA-4 | 20x20 | 52 | 57.5 | 45 | 20
| CVA-5 | 20x20 | 52 | 65 | 40 | 16
| EAH-1 | 20x20 | 52 | 56 | 57 | 48
| EAH-2 | 20x20 | 52 | 74 | 45 | 30
| EAH-3 | 20x20 | 52 | 46 | 80 | 55
| EC-1 | 20x20 | 52 | 56 | 57 | 48
| EC-2 | 20x20 | 52 | 74 | 45 | 30
| EC-3 | 20x20 | 52 | 46 | 80 | 55
| EVA-1 | 20x20 | 52 | 35 | 65 | 48
| EVA-2 | 20x20 | 52 | 46.2 | 53 | 30
| EVA-3 | 20x20 | 52 | 28.8 | 88 | 55
| EVA-4 | 20x20 | 52 | 57.5 | 45 | 20
| EVA-5 | 20x20 | 52 | 65 | 40 | 16
| EVAC-1 | 20x20 | 52 | 35 | 65 | 48
| EVAC-2 | 20x20 | 52 | 46.2 | 53 | 30
| EVAC-3 | 20x20 | 52 | 28.8 | 88 | 55
| EVAC-4 | 20x20 | 52 | 57.5 | 45 | 20
| EVAC-5 | 20x20 | 52 | 65 | 40 | 16
| L-1C | 20x20 | 35 | 40.8 | 57 | 45
| L-1X | 20x20 | 35 | 40.8 | 57 | 45
| L-1X16 | 20x20 | 35 | 40.8 | 57 | 45
| VA-1 | 20x20 | 52 | 35 | 65 | 48
| VA-2 | 20x20 | 52 | 46.2 | 53 | 30
| VA-3 | 20x20 | 52 | 28.8 | 88 | 55
| VA-4 | 20x20 | 52 | 57.5 | 45 | 20
| VA-5 | 20x20 | 52 | 65 | 40 | 16
Double Tank Stationary Rack, Chemical Sanitizing
| B-1 | 20x20 | N/A | 89.6 | 57 | 48
| B-2 | 20x20 | N/A | 118.4 | 45 | 30
| B-3 | 20x20 | N/A | 73.6 | 80 | 55
| CB-1 | 20x20 | N/A | 89.6 | 57 | 48
| CB-2 | 20x20 | N/A | 118.4 | 45 | 30
| CB-3 | 20x20 | N/A | 70.4 | 80 | 55
Single Tank Stationary Rack, Hot Water Sanitizing
| CMA-180 HTC | 20x20 |  | 50 | 49 | 12
| CMA-180 HTCB | 20x20 |  | 50 | 49 | 12
| CMA-180 HTS | 20x20 |  | 52 | 49 | 12
| CMA-180 HTSB | 20x20 |  | 52 | 49 | 12
| CMA-180-THTC | 20x20 | 1.24 | 74.4 | 44 | 11
| CMA-180-THTCB | 20x20 | 1.24 | 74.4 | 44 | 11
| CMA-180-THTS | 20x20 | 1.24 | 74.4 | 44 | 11
| CMA-180-THTSB | 20x20 | 1.24 | 74.4 | 44 | 11
Undercounter, Hot Water Sanitizing
| CMA-180 UC | 20x20 | 3.22 | 20.6 | 94 | 16
Compact Warewashing Station, Chemical Sanitizing
| CWS-1 | 20x20 | 52 | 56 | 57 | 48
| CWS-2 | 20x20 | 52 | 74 | 45 | 30
| CWS-3 | 20x20 | 52 | 46 | 80 | 55
DOUGLAS MACHINES CORPORATION
STATIONARY RACK POT, PAN, AND UTENSIL WASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
Single Tank Stationary Rack - Hot Water Sanitizing
| LD-10 | 24x27 | 7.6 | 27.8 | 240 | 22
| SD-10 | 24x27 | 7.6 | 27.8 | 240 | 22
| LD-10-PT | 27x28 | 7.6 | 31.7 | 240 | 27
| LD-12-CPT | 27x28 | 7.6 | 31.7 | 240 | 27
| LD-15 | 27x38 | 11.4 | 47.5 | 240 | 27
| SD-16 | 27x38 | 11.4 | 47.5 | 240 | 27
| SD-20 | 27x38 | 11.4 | 47.5 | 240 | 27
| 1527-N | 34x63 | 24 | 100.0 | 240 | 30
| 1536-B | 41x63 | 24 | 120.0 | 240 | 30
| 1536-N | 41x63 | 24 | 120.0 | 240 | 30
| 3072-N | 63x72 | 40 | 200.0 | 240 | 30
| D-UTM-10 | 25x27 | 5.7 | 35.0 | 254 | 37
ECOLAB, INC.
CONVEYOR DISHWASHING MACHINES
| Model | Conveyor | Flow | Usage | (Max.)
| Number | Width | gpm | gph | (ft/min.)
Single Tank Conveyor Chemical Sanitizing
| ET44 | 20x20 | 4.84 | 290 | 5.8
STATIONARY RACK DISHWASHING MACHINES
Single Tank Door Chemical Sanitizing
| SLC-20 | 20x20 | 68 | 63 | 40 | 20
ECOLAB, INC.
CONVEYOR DISHWASHING MACHINES
| Model | Conveyor | Flow | Usage | (Max.)
| Number | Width | gpm | gph | (ft/min.)
Single Tank Rack Conveyor Dishmachines - Hot Water Sanitizing
| ES-4400 | 20x20 | 3.9 | 234 | 6.9
| ES-6600 | 20x20 | 3.9 | 234 | 6.9
| ES-8000 | 20x20 | 3.9 | 234 | 6.9
| PA-C4 | 20x20 | 3.89 | 233 | 6
| WH-44 | 20x20 | 3.89 | 233 | 6
| WH-44CSS | 20x20 | 3.89 | 233 | 6
| WH-66 | 20x20 | 3.89 | 233 | 6
Single Tank Rack Conveyor Dishmachines - Chemical Sanitizing
| ES-4400CS | 20x20 | 3.9 | 234 | 6.5
| ES-6600CS | 20x20 | 3.9 | 234 | 6.5
| ES-8000CS | 20x20 | 3.9 | 234 | 6.5
| PA-C4-CS | 20x20 | 3.89 | 233 | 6
| WH-44CS | 20x20 | 3.89 | 233 | 6
| WH-66CS | 20x20 | 3.89 | 233 | 6
STATIONARY RACK DISHWASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
Single Tank Chemical Sanitizing Dishmachines
| ES-1000HN | 20x20 | 6.6 | 28.8 | 56 | 35
| ES-1000N | 20x20 | 6.6 | 28.8 | 56 | 35
| ES-1000N/B | 20x20 | 6.6 | 28.8 | 56 | 35
| ES-2000 | 20x20 |  | 57.6 | 40 | 15
| ES-2000 | 20x20 |  | 48 | 40 | 25
| ES-2000-CS | 20x20 | N/A | 48 | 40 | 25
| ES-2000-CS | 20x20 | N/A | 57.6 | 40 | 15
| ES-2000XSP | 20x20 |  | 57.6 | 40 | 15
| ES-2000XSP | 20x20 |  | 48 | 40 | 25
| ES-2000XSP-PH | 20x20 |  | 57.6 | 40 | 25
| ES-2000XSP-TB | 20x20 |  | 48 | 40 | 25
| ES-4000 | 2(20x20) |  | 144 | 35 | 20
| ES-4000 | 2(20x20) |  | 120 | 40 | 25
| ES-4000XSP | 2(20x20) |  | 144 | 35 | 20
| ES-4000XSP | 2(20x20) |  | 120 | 40 | 25
| Omega | 20x20 | N/A | 48 | 43 | 25
| Omega 5 | 20x20 | N/A | 36 | 46 | 25
| Omega CS | 20x20 | N/A | 55.7 | 42 | 15
| Omega XSP | 20x20 | N/A | 48 | 43 | 25
| PA-1 | 20x20 |  | 57.6 | 40 | 15
| PA-2 | 2(20x20) |  | 144 | 35 | 20
| PA-U | 20x20 | 6.6 | 28.8 | 56 | 35
| PA-UN | 20x20 | 6.6 | 28.8 | 56 | 35
| PA-UNB | 20x20 | 6.6 | 28.8 | 56 | 35
| Typhoon | 20x20 | N/A | 55.7 | 42 | 15
Single Tank Door Dishmachines - Hot Water Sanitizing
| ES-18 | 20x20 | 5.46 | 57 | 45 | 11
| ES-18HT | 20x20 | 5.46 | 57 | 45 | 11
| Inferno | 20x20 | N/A | 69 | 41 | 11
| Omega HT | 20x20 | N/A | 69 | 41 | 11
| PA-HT | 20x20 | 5.46 | 72 | 45 | 15
| Performer | 20x20 | 7.2 | 70.8 | 35 | 10
Single Tank Door Dishmachines - Hot Water and Chemical Sanitizing
| Huey 165 | 20x20 | 7.6 | 52 | 40 | 25
| Supra-Q2020 | 20x20 | 7.6 | 52 | 40 | 25
Single Tank Chemical Sanitizing Dishmachines
| ES-1000 | 20x20 | 6.6 | 28.8 | 56 | 35
HOBART CORPORATION
STATIONARY RACK DISHWASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
Single Tank Chemical Sanitizing Door
| AM-14 | 20x20 | 8 | 74.4 | 40 | 9
| AM-14 | 20x20 | 8 | 96 | 27 | 9
| AM-14C | 20x20 | 8 | 72 | 40 | 9
| AM-14C | 20x20 | 8 | 91.2 | 27 | 9
| AM-14F | 20x20 | 5.67 | 56.8 | 40 | 15
| AM-14F | 20x20 | 5.67 | 66.7 | 27 | 15
| AM-14T | 20x20 | 5.67 | 79.5 | 40 | 15
| AM-14T | 20x20 | 5.67 | 99.4 | 27 | 15
| AM-14TC | 20x20 | 5.67 | 95.1 | 27 | 15
| AM-14TC | 20x20 | 5.67 | 76.7 | 40 | 15
| LT-1 | 20x20 | 62 | 70.3 | 41 | 22
Single Tank Chemical Sanitizing Door (Dual Sanitizing Mode Machines)
| AM15 | 20x20 | 4.4 | 47.4 | 38 | 10
| AM15F | 20x20 | 4.4 | 33 | 38 | 10
| AM15T | 20x20 | 4.4 | 47.4 | 38 | 10
Single Tank Door
| AM-14 | 20x20 | 8 | 63.6 | 40 | 9
| AM-14C | 20x20 | 8 | 62.4 | 40 | 9
| AM-14F | 20x20 | 5.67 | 51.1 | 40 | 15
| AM-14T | 20x20 | 5.67 | 69.6 | 40 | 15
| AM-14TC | 20x20 | 5.67 | 68.2 | 40 | 15
Single Tank Door (Dual Sanitizing Mode Machines)
| AM15 | 20x20 | 4.4 | 42.3 | 38 | 10
| AM15F | 20x20 | 4.4 | 33 | .8 | 10
| AM15T | 20x20 | 4.4 | 42.3 | 38 | 10
Single Tank Door Chemical Sanitizing, Dump-Type
| LX-18C | 20x20 | N/A | 37.5 | 115 | 15
| LX-18C | 20x20 | N/A | 72.8 | 70 | 15
Single Tank Door, Chemical Sanitizing, Fresh Water Rinse, 2 Temperature
| LX-30C | 20x20 | 6 | 28.8 | 85 | 10
| LX-40C | 20x20 | 6 | 36 | 55 | 10
| LX-GC | 20x20 | 6 | 36 | 55 | 10
| LXiC | 20x20 | 6 | 28.8 | 85 | 10
| LXiGC | 20x20 | 6 | 36 | 55 | 10
Single Tank Door, Dump-Type
| LX-18 | 20x20 | N/A | 72.8 | 70 | 15
| LX-18H, LX-18 | 20x20 | N/A | 37.5 | 115 | 15
Single Tank Door, Fresh Water Rinse, Two Temperature
| LX-30H, LX-30 | 20x20 | 6 | 28.8 | 85 | 10
| LX-40H | 20x20 | 6 | 36 | 55 | 10
| LX-GH | 20x20 | 6 | 36 | 55 | 10
| LXiGH | 20x20 | 6 | 36 | 55 | 10
| LXiH | 20x20 | 6 | 28.8 | 85 | 10
Single Tank Hood
| SM-6T2 | 16x16 | 6.8 | 52 | 73 | 12
STATIONARY RACK POT, PAN, AND UTENSIL WASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
Single Tank Chemical Sanitizing Door (Dual Sanitizing Mode Machines)
| AM15 | 20x20 | 4.4 | 18.9 | 120 | 10
| AM15F | 20x20 | 4.4 | 16.1 | 120 | 10
| AM15T | 20x20 | 4.4 | 18.9 | 120 | 10
Single Tank Door (Dual Sanitizing Mode Machines)
| AM15 | 20x20 | 4.4 | 18.2 | 120 | 10
| AM15F | 20x20 | 4.4 | 15.4 | 120 | 10
| AM15T | 20x20 | 4.4 | 18.2 | 120 | 10
CONVEYOR DISHWASHING MACHINES
Multiple Tank Rackless Conveyor, Hot Water Sanitizing
| FT900 | 30.5 | 5.4 | 324 | 12
| FT900W | 30.5 | 3.3 | 198 | 12
| FT900W | 30.5 | 3.3 | 198 | 10
Single Tank Rackless Conveyor, Hot Water Sanitizing
| FT900S | 30.5 | 6.5 | 390 | 6.3
CONVEYOR DISHWASHING MACHINES
| Model | Conveyor | Flow | Usage | (Max.)
| Number | Width | gpm | gph | (ft/min.)
Multiple Tank Rack Conveyor Chemical Sanitizing
| C-64A | 20x20 | 4.6 | 278 | 6.9
| C-64A | 20x20 | 2.4 | 145 | 6.9
| C-64W | 20x20 | 3.2 | 192 | 6.9
| CCS-86A | 20x20 | 4.6 | 278 | 6.9
| CCS-86A | 20x20 | 2.4 | 145 | 6.9
| CCS-86W | 20x20 | 3.2 | 192 | 6.9
| CPW-100A | 20x20 | 4.6 | 278 | 6.9
| CPW-100A | 20x20 | 2.4 | 145 | 6.9
| CPW-100W | 20x20 | 3.2 | 192 | 6.9
| CRS-86A | 20x20 | 4.6 | 278 | 6.9
| CRS-86A | 20x20 | 2.4 | 145 | 6.9
| CRS-86W | 20x20 | 3.2 | 192 | 6.9
Multiple Tank Rack Conveyor, Hot Water Sanitizing
| C-64A | 20x20 | 4.6 | 278 | 6.9
| C-64A | 20x20 | 2.4 | 145 | 6.9
| C-64W | 20x20 | 3.2 | 192 | 6.9
| CCS-86A | 20x20 | 4.6 | 278 | 6.9
| CCS-86A | 20x20 | 2.4 | 145 | 6.9
| CCS-86W | 20x20 | 3.2 | 192 | 6.9
| CPW-100A | 20x20 | 4.6 | 278 | 6.9
| CPW-100A | 20x20 | 2.4 | 145 | 6.9
| CPW-100W | 20x20 | 3.2 | 192 | 6.9
| CRS-86A | 20x20 | 2.4 | 145 | 6.9
| CRS-86A | 20x20 | 4.6 | 278 | 6.9
| CRS-86W | 20x20 | 3.2 | 192 | 6.9
Single Tank Rack Conveyor Chemical Sanitizing
| C-44A | 20x20 | 5 | 300 | 5.6
| C-44A | 20x20 | 2.5 | 149 | 5.6
| C-44AW | 20x20 | 2 | 120 | 3.5
| C-44AW | 20x20 | 1.36 | 82 | 3.5
| C-54A | 20x20 | 5.2 | 312 | 7
| C-54A | 20x20 | 2.5 | 153 | 6.9
| CCS-66A | 20x20 | 5 | 300 | 5.6
| CCS-66A | 20x20 | 2.5 | 149 | 5.6
| CCS-66AW | 20x20 | 2 | 120 | 3.5
| CCS-66AW | 20x20 | 1.36 | 82 | 3.5
| CCS-76A | 20x20 | 5.2 | 312 | 7
| CCS-76A | 20x20 | 2.5 | 153 | 6.9
| CMT44 | 20x20 | 4.6 | 276 | 5.9
| CMT66 | 20x20 | 4.6 | 276 | 5.9
| CPW-80A | 20x20 | 5 | 300 | 5.6
| CPW-80A | 20x20 | 2.5 | 149 | 5.6
| CPW-80AW | 20x20 | 1.36 | 82 | 3.5
| CPW-80AW | 20x20 | 2 | 120 | 3.5
| CPW-90A | 20x20 | 5.2 | 312 | 7
| CPW-90A | 20x20 | 2.5 | 153 | 6.9
| CRS-66A | 20x20 | 5 | 300 | 5.6
| CRS-66A | 20x20 | 2.5 | 149 | 5.6
| CRS-66AW | 20x20 | 2 | 120 | 3.5
| CRS-66AW | 20x20 | 1.36 | 82 | 3.5
| CRS-76A | 20x20 | 5.2 | 312 | 7
| CRS-76A | 20x20 | 2.5 | 153 | 6.9
Single Tank Rack Conveyor, Hot Water Sanitizing
| C-44A | 20x20 | 5 | 300 | 5.6
| C-44A | 20x20 | 2.5 | 149 | 5.6
| C-44AW | 20x20 | 2 | 120 | 3.5
| C-44AW | 20x20 | 1.3 | 80 | 3.5
| C-54A | 20x20 | 2.5 | 153 | 6.9
| C-54A | 20x20 | 6.2 | 372 | 7
| CCS-66A | 20x20 | 5 | 300 | 5.6
| CCS-66A | 20x20 | 2.5 | 149 | 5.6
| CCS-66AW | 20x20 | 2 | 120 | 3.5
| CCS-66AW | 20x20 | 1.36 | 82 | 3.5
| CCS-76A | 20x20 | 2.5 | 153 | 6.9
| CCS-76A | 20x20 | 6.2 | 372 | 7
| CMT44 | 20x20 | 4.6 | 276 | 5.9
| CMT66 | 20x20 | 4.6 | 276 | 5.9
| CPW-80A | 20x20 | 5 | 300 | 5.6
| CPW-80A | 20x20 | 2.5 | 149 | 5.6
| CPW-80AW | 20x20 | 2 | 120 | 3.5
| CPW-80AW | 20x20 | 1.36 | 82 | 3.5
| CPW-90A | 20x20 | 6.2 | 372 | 7
| CPW-90A | 20x20 | 2.5 | 153 | 6.9
| CRS-66A | 20x20 | 5 | 300 | 5.6
| CRS-66A | 20x20 | 2.5 | 149 | 5.6
| CRS-66AW | 20x20 | 2 | 120 | 3.5
| CRS-66AW | 20x20 | 1.36 | 82 | 3.5
| CRS-76A | 20x20 | 6.2 | 372 | 7
| CRS-76A | 20x20 | 2.5 | 153 | 6.9
STATIONARY RACK DISHWASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
Single Tank Chemical Sanitizing Door
| AM-14 | 20x20 | 8.85 | 89.7 | 40 | 10
| AM-14C | 20x20 | 8.85 | 89.7 | 40 | 10
| AM-14F | 20x20 | 5.67 | 56.8 | 40 | 15
| AM-14F | 20x20 | 5.67 | 66.7 | 27 | 15
| AM-14T | 20x20 | 5.67 | 79.5 | 40 | 15
| AM-14T | 20x20 | 5.67 | 99.4 | 27 | 15
| AM-14TC | 20x20 | 5.67 | 76.7 | 40 | 15
| AM-14TC | 20x20 | 5.67 | 95.1 | 27 | 15
| SR24C | 20x20 |  | 33.9 | 102 | 28
Single Tank Door, Hot Water Sanitizing
| AM-14 | 20x20 | 8.85 | 89.7 | 40 | 10
| AM-14C | 20x20 | 8.85 | 89.7 | 40 | 10
| AM-14F | 20x20 | 5.67 | 51.1 | 40 | 15
| AM-14T | 20x20 | 5.67 | 69.6 | 40 | 15
| AM-14TC | 20x20 | 5.67 | 68.2 | 40 | 15
| SR24 | 20x20 |  | 39 | 76 | 31
| SR24H | 20x20 |  | 39 | 76 | 31
STATIONARY RACK POT, PAN, AND UTENSIL WASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
| UW-50 | 2(20x20) | 10.3 | 74.4 | 132 | 24
CONVEYOR DISHWASHING MACHINES
Multiple Tank Rack Conveyor, Hot Water Sanitizing
| C-64A | 20x20 | 4.6 | 278 | 6.9
Multiple Tank rack Conveyor Chemical Sanitizing
| C-64A | 20x20 | 4.6 | 278 | 6.9
Single Tank Rack Conveyor Chemical Sanitizing
| C-44A | 20x20 | 5 | 300 | 5.6
| C-44AW | 20x20 | 2 | 120 | 3.5
Single Tank Rack Conveyor, Hot Water Sanitizing
| C-44A | 20x20 | 5 | 300 | 5.6
| C-44AW | 20x20 | 2 | 120 | 3.5
STATIONARY RACK DISHWASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
Single Tank Chemical Sanitizing Door
| AM-14 | 20x20 | 8 | 96 | 27 | 9
| AM-14 | 20x20 | 8 | 74.4 | 40 | 9
| AM-14C | 20x20 | 8 | 72 | 40 | 9
| AM-14C | 20x20 | 8 | 91.2 | 27 | 9
| AM-14F | 20x20 | 5.67 | 56.8 | 40 | 15
| AM-14F | 20x20 | 5.67 | 66.7 | 27 | 15
| AM-14T | 20x20 | 5.67 | 79.5 | 40 | 15
| AM-14T | 20x20 | 5.67 | 99.4 | 27 | 15
| AM-14TC | 20x20 | 5.67 | 76.7 | 40 | 15
| AM-14TC | 20x20 | 5.67 | 95.1 | 27 | 15
| LT-1 | 20x20 | 62 | 70.3 | 41 | 22
Single Tank Door
| AM-14 | 20x20 | 8 | 63.6 | 40 | 9
| AM-14C | 20x20 | 8 | 62.4 | 40 | 9
| AM-14F | 20x20 | 5.67 | 51.1 | 40 | 15
| AM-14T | 20x20 | 5.67 | 69.6 | 40 | 15
| AM-14TC | 20x20 | 5.67 | 68.2 | 40 | 15
HOBART GMBH
CONVEYOR DISHWASHING MACHINES
| Model | Conveyor | Flow | Usage | (Max.)
| Number | Width | gpm | gph | (ft/min.)
Multiple Tank Rackless Conveyor
| FTX TCL1 S A TCU1 C1 | 20 | 2 | 120 | 4
D2AT US
| FTX 9 S B 3 C1 D2AT US | 24 | 2.1 | 126 | 6.3
| FTN 6/4 X S A DS Y US | 24 | 2.8 | 170 | 5
| FTN 6/4 X S A DS Y US | 24 | 2.8 | 170 | 5
| FTN 6/4 X S B DS Y US | 24 | 3.8 | 228 | 7
| FTN 6/4 X S B DS Y US | 24 | 3.8 | 228 | 7
| FTN 6/5 X S B DS Y US | 24 | 3.6 | 217 | 7
| FTN 6/5 X S B DS Y US | 24 | 3.6 | 217 | 7
| FTN 8/5 X S B DS Y US | 31.7 | 4.6 | 276 | 7
| FTN 8/5 X S B DS Y US | 31.7 | 4.6 | 276 | 7
| FTN 8/5 X S C DS Y US | 31.7 | 4.9 | 298 | 10
| FTN 8/5 X S C DS Y US | 31.7 | 4.9 | 298 | 10
Multiple Tank Rack Conveyors[6]
| CN A CDS US | 20 | 2.5 | 147 | 3.3
| CN EA CDS US | 20 | 2.5 | 147 | 4.9
| CN LA CDS US | 20 | 2.5 | 147 | 4.9
STATIONARY RACK DISHWASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
Single Tank Stationary Rack Hot Water Sanitizing
| AMX70 US | 20x20 | 7.71 | 74.9 | 26 | 11
| FX40 US | 20x20 | 6.87 | 36.5 | 60 | 11
INSINGER MACHINE COMPANY (THE)
CONVEYOR DISHWASHING MACHINES
| Model | Conveyor | Flow | Usage | (Max.)
| Number | Width | gpm | gph | (ft/min.)
Single Tank Rack Conveyor, Hot Water Sanitizing
| Admiral 44-4 | 20x20 | 2.7 | 162 | 6.4
| Admiral 66-4 | 20x20 | 2.7 | 162 | 6.4
Tray Washer Multiple Tank Conveyor, Hot Water Sanitizing
| TRAC 321-2 | N/A | 4.14 | 248 | 11
| TRAC-878 | N/A | 3.28 | 196.64 | 18.3
Multiple Tank Rack Conveyor, Hot Water Sanitizing
| 135-20 | 20x20 | 4.0 | 240 | 3.7
| 185-20 | 20x20 | 4.0 | 240 | 5.1
| 250-20 | 20x20 | 4.0 | 240 | 7
| 60-20 | 20x20 | 4.0 | 240 | 1.6
| 85-20 | 20x20 | 4.0 | 240 | 2.3
| R-106-2 | 20x20 | 2 | 240 | 10
| Speeder 64 | 20x20 | 3.7 | 222 | 7.7
| Speeder 86-3 | 20x20 | 3.7 | 222 | 7.7
| Super 106-2 | 20x20 | 4 | 240 | 9.2
Multiple Tank Rackless Conveyor, Hot Water Sanitizing
| Century 14 | 26 | 3.8 | 228 | 7
| Clipper RC-##-RPW-W | 26 | 3.7 | 222 | 6.8
| Defender-(1) | 26 | 5.1 | 306 | 7.1
| Master RC-(1)-RPW-W3 | 26 | 5.2 | 312 | 10.5
| Master RC-(1)-RPW-W4 | 31 | 5.33 | 320 | 12.3
STATIONARY RACK DISHWASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
Single Tank Hood, Hot Water Sanitizing
| 45SA-5 | 16x16 | 4.1 | 36 | 38 | 12
| Ensign 40-2 Automatic | 16x16 | 8 | 61 | 60 | 12
Hot Water Single Tank Stationary Rack
| 50-20N2-NSU | 20x20 | 3.0 | 60 | 30 | 20
| Commander 18-5 | 20x20 | 3.0 | 60 | 30 | 20
| Commander 18-5C | 20x20 | 3.0 | 58 | 30 | 20
| Commander 18-5CH | 20x20 | 3.0 | 58 | 30 | 20
| Commander 18-5H | 20x20 | 3.0 | 60 | 30 | 20
Undercounter Hot Water Sanitizing
| GS 302 | 20x20 | N/A | 13.5 | 133 | 11
| GS-14 | 20x20 | N/A | 9.6 | 124 | 12
Single Tank Chemical Sanitizing
| CS-5 | 20x20 | 3.0 | 60 | 30 | 20
| CS-5C | 20x20 | 3.0 | 58 | 30 | 20
| CS-5CH | 20x20 | 3.0 | 58 | 30 | 20
| CS-5H | 20x20 | 3.0 | 60 | 30 | 20
STATIONARY RACK POT, PAN, AND UTENSIL WASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
Single Tank Stationary Rack - Hot Water Sanitizing
| CA-3 | 24x28 | 11.2 | 70 | 120 | 15
| DA-3 | 2*24x28 | 22.4 | 140 | 120 | 15
JACKSON MSC
CONVEYOR DISHWASHING MACHINES
| Model | Conveyor | Flow | Usage | (Max.)
| Number | Width | gpm | gph | (ft/min.)
Single Tank Rack Conveyor - Hot Water Sanitizing
| AJ-44 | 20x20 | 3.9 | 234 | 6.9
| AJ-54 | 20x20 | 4.6 | 279 | 7.5
| AJ-66 | 20x20 | 3.9 | 234 | 6.9
| AJ-76 | 20x20 | 4.6 | 279 | 7.5
| AJ-80 | 20x20 | 3.9 | 234 | 6.9
| AJ-90 | 20x20 | 4.6 | 279 | 7.5
| ES-4400 | 20x20 | 3.9 | 234 | 6.9
| ES-6600 | 20x20 | 3.9 | 234 | 6.9
| ES-8000 | 20x20 | 3.9 | 234 | 6.9
| PA-C4 | 20x20 | 3.89 | 233 | 6
| WH-44 | 20x20 | 3.89 | 233 | 6
| WH-66 | 20x20 | 3.89 | 233 | 6
Multiple Tank Rack Conveyor - Hot Water Sanitizing
| AJ-100 | 20x20 | 3.7 | 222 | 8
| AJ-64 | 20x20 | 3.7 | 222 | 8
| AJ-86 | 20x20 | 3.7 | 222 | 8
Multiple Tank Rackless Conveyor - Hot Water Sanitizing
| JFT | 29 | 3.6 | 216 | 8.6
| JFT-G | 29 | 3.6 | 216 | 8.6
| JFT-S | 29 | 3.6 | 216 | 8.6
Single Tank Rack Conveyor - Chemical Sanitizing
| AJ-44 | 20x20 | 3.9 | 234 | 6.5
| AJ-66 | 20x20 | 3.9 | 234 | 6.5
| AJ-80 | 20x20 | 3.9 | 234 | 6.9
| ES-4400 | 20x20 | 3.9 | 234 | 6.5
| ES-6600 | 20x20 | 3.9 | 234 | 6.5
| ES-8000 | 20x20 | 3.9 | 234 | 6.5
| PA-C4-CS | 20x20 | 3.9 | 233 | 6
| WH-44 | 20x20 | 3.89 | 233 | 6
| WH-44CS | 20x20 | 3.89 | 233 | 6
| WH-66 | 20x20 | 3.89 | 233 | 6
STATIONARY RACK DISHWASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
Single Tank Hood - Hot Water Sanitizing
| 10A | 17xdia. | 7.8 | 58 | 60 | 10
| 10APRB | 17xdia. | 7.8 | 58 | 60 | 10
| 10APRB-M | 17xdia. | 7.8 | 58 | 60 | 10
| 10U | 17xdia. | 7.8 | 58 | 60 | 10
Single Tank Door - Hot Water Sanitizing
| 200 | 20x20 | 5 | 52.2 | 45 | 11
| 300X | 20x20 | 5.46 | 57 | 45 | 11
| 300XN | 20x20 | 5.46 | 57 | 45 | 11
| E-xxion | 20x20 | 5.46 | 57 | 45 | 11
| ES-18 | 20x20 | 5.46 | 57 | 45 | 11
| ES-18HT | 20x20 | 5.46 | 57 | 45 | 11
| H-24 | 20x20 | 5.7 | 25.8 | 117 | 13
| HZ-24 | 20x20 | 5.7 | 25.8 | 117 | 13
| Inferno | 20x20 | N/A | 69 | 41 | 11
| JP-24 | 20x20 | 6.6 | 26.4 | 82 | 10
| JPX-300H | 20x20 | 6.6 | 26.4 | 82 | 10
| JPX-300HN | 20x20 | 6.6 | 26.4 | 82 | 10
| M-24BF | 20x20 | 6.6 | 26.4 | 82 | 10
| Omega HT | 20x20 | N/A | 69 | 41 | 11
| PA-HT | 20x20 | 5.46 | 72 | 45 | 15
| Performer | 20x20 | 7.2 | 70.8 | 35 | 10
| TS-57 | 20x20 | 5.46 | 57 | 45 | 11
| TempStar | 20x20 | 5.46 | 57 | 45 | 11
| TempStar HH | 20x20 | 5.46 | 72 | 45 | 15
| TempStar HH/S | 20x20 | 5.46 | 72 | 45 | 11
Single Tank Door - Hot Water and Chemical Sanitizing
| Huey 165 | 20x20 | 7.6 | 52 | 40 | 25
| Supra-Q2020 | 20x20 | 7.6 | 52 | 40 | 25
Single Tank Door - Chemical Sanitizing
| Cleanware I | 20x20 | 55 | 111 | 50 | 20
| Cleanware II | 2(20x20) | 62.5 | 188 | 47 | 28
| Conserver I | 20x20 | 55 | 111 | 50 | 20
| Conserver II | 2(20x20) | 62.5 | 188 | 47 | 18
| Conserver XL | 20x20 | N/A | 55 | 42 | 25
| Conserver XL2 | 2(20x20) | N/A | 144 | 35 | 20
| Conserver XL2 | 2(20x20) | N/A | 120 | 40 | 25
| Delta 5 | 20x20 | N/A | 36 | 46 | 25
| ES-1000HN | 20x20 | 6.6 | 28.8 | 56 | 35
| ES-1000N | 20x20 | 6.6 | 28.8 | 56 | 35
| ES-1000N/B | 20x20 | 6.6 | 28.8 | 56 | 35
| ES-2000 | 20x20 | N/A | 48 | 40 | 25
| ES-2000 | 20x20 | N/A | 57.6 | 40 | 15
| ES-2000-CS | 20x20 | N/A | 48 | 40 | 25
| ES-2000-CS | 20x20 | N/A | 57.6 | 40 | 15
| ES-2000XSP-PH | 20x20 | N/A | 48 | 40 | 25
| ES-2000XSP-TB | 20x20 | N/A | 48 | 40 | 25
| ES-4000 | 2(20x20) | N/A | 120 | 40 | 25
| ES-4000 | 2(20x20) | N/A | 144 | 35 | 20
| JPX-300LP | 20x20 | 6.6 | 28.8 | 56 | 35
| JPX-300LPB | 20x20 | 6.6 | 28.8 | 56 | 35
| Omega | 20x20 | N/A | 48 | 43 | 25
| Omega 5 | 20x20 | N/A | 36 | 46 | 25
| Omega CS | 20x20 | N/A | 55.7 | 42 | 15
| PA-1 | 20x20 | N/A | 57.6 | 40 | 15
| PA-2 | 2(20x20) | N/A | 144 | 35 | 20
| PA-U | 20x20 | 6.6 | 28.8 | 56 | 35
| PA-UN | 20x20 | 6.6 | 28.8 | 56 | 35
| PA-UNB | 20x20 | 6.6 | 28.8 | 56 | 35
| Typhoon | 20x20 | N/A | 55.7 | 42 | 15
Single Tank Door - Chemical Sanitizing
| 200LT | 20x20 | 4.6 | 51.3 | 45 | 11
| 300XLT | 20x20 | 6.5 | 73 | 45 | 12
| Conserver 24LTP | 20x20 | 6.6 | 28.8 | 56 | 35
| JPX-300L | 20x20 | 6.6 | 28.8 | 56 | 35
| TempStar LT | 20x20 | 6.5 | 73 | 45 | 12
Single Tank Chemical Sanitizing
| Conserver 24LT | 20x20 | 6.6 | 28.8 | 56 | 35
| ES-1000 | 20x20 | 6.6 | 28.8 | 56 | 35
| ES-1000H | 20x20 | 6.6 | 28.8 | 56 | 35
CONVEYOR DISHWASHING MACHINES
| Model | Conveyor | Flow | Usage | (Max.)
| Number | Width | gpm | gph | (ft/min.)
Single Tank Rackless Conveyor - Hot Water Sanitizing
| BA 532 PG-N | 28.5 | 3.95 | 237 | 10.0
| B 230 VP-N | 23.4 | 2.99 | 179 | 8.0
| B 230 VAP-N | 23.4 | 2.99 | 179 | 8.0
Multiple Tank Rackless Conveyor - Hot Water Sanitizing
| BA 533 PG-N | 28.5 | 3.95 | 237 | 12.0
| BA 534 PG-N | 28.5 | 3.95 | 237 | 13.6
| B 460 VP-N | 23.4 | 2.99 | 179 | 8.2
| B 460 VAP-N | 23.4 | 2.99 | 179 | 8.2
| B 690 VP-N | 23.4 | 2.99 | 179 | 8.2
| B 690 VAP-N | 23.4 | 2.99 | 179 | 8.2
JACKSON MSC
STATIONARY RACK DISHWASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
Single Tank Undercounter
| CJ-14 | 14x14 | 2.10 | 6.4 | 226 | 14
| CJ-16 | 16x16 | 1.56 | 18.7 | 107 | 14
| CJ-20 | 20x20 | 3.92 | 23.5 | 105 | 15
| CJ-20/2 | 20x20 | 3.92 | 23.5 | 105 | 15
KNIGHT, INC.
STATIONARY RACK DISHWASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
Single Tank Stationary Rack Hot Water Sanitizing
| KLE 112HL | 20x20 | 6.9 | 70 | 46 | 11
Single Tank Stationary Rack Chemical Sanitizing
| KLE 112HL | 20x20 | 6.9 | 70 | 46 | 11
| KLE 117i | 20x20 | 49 | 86 | 47 | 28
| KLE 117c | 20x20 | 49 | 86 | 47 | 28
| KLE 235d | 20x20 | 98 | 129.5 | 47 | 28
| KLE 175GT | 20x20 | 49 | 86 | 47 | 28
| KLE 175GT | 20x20 | 7.8 | 99 | 37 | 24
| KLE 175GTM | 20x20 | 49 | 86 | 47 | 28
| KLE 175GTM | 20x20 | 7.8 | 99 | 37 | 24
Under Counter Chemical Sanitizing Dishmachine
| KLE 115U | 20x20 | 6.2 | 57 | 45 | 28
| KLE 150GT | 20x20 | 10 | 81 | 45 | 29
LVO MANUFACTURING, INC.
STATIONARY RACK POT, PAN, AND UTENSIL WASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
Single Tank Stationary Rack - Hot Water Sanitizing
| CL-10 | 28x29 | 4.5 | 49.5 | 180 | 60
| FL 25 | 26x29 | 7.1 | 94.6 | 180 | 40
| FL 36 | 33x73 | 16.2 | 162 | 180 | 40
| FL-10 | 28x29 | 4.5 | 49.5 | 180 | 60
| FL-14 | 31.5x37 | 5.0 | 65 | 180 | 60
| PT 25 | 26x29 | 7.1 | 94.6 | 180 | 40
| PT-10 | 28x29 | 4.5 | 49.5 | 180 | 60
| PT-14 | 31.5x37 | 5.0 | 65 | 180 | 60
| RW 1548 | 45x75 | 14 | 168 | 180 | 60
| RW 2580 | 2*33x70 | 26 | 311 | 180 | 60
MEIKO MASCHINENBAU GMBH & CO.
CONVEYOR DISHWASHING MACHINES
| Model | Conveyor | Flow | Usage | (Max.)
| Number | Width | gpm | gph | (ft/min.)
Single Tank Rack Conveyor - Hot Water Sanitizing[1] [2]
| K-44E | 20x20 | 3.10 | 186 | 6.14
| K-66E | 20x20 | 3.10 | 186 | 6.14
| K-80E | 20x20 | 3.10 | 186 | 6.14
| K-44S | 20x20 | 3.10 | 186 | 6.14
| K-66S | 20x20 | 3.10 | 186 | 6.14
| K-80S | 20x20 | 3.10 | 186 | 6.14
| K-54E | 20x20 | 3.90 | 234 | 7.23
| K-76E | 20x20 | 3.90 | 234 | 7.23
| K-90E | 20x20 | 3.90 | 234 | 7.23
| K-54S | 20x20 | 3.90 | 234 | 7.23
| K-76S | 20x20 | 3.90 | 234 | 7.23
| K-90S | 20x20 | 3.90 | 234 | 7.23
Multiple Tank Rack Conveyor - Hot Water Sanitizing[1] [2]
| K-64E | 20x20 | 3.83 | 230 | 7.70
| K-86E | 20x20 | 3.83 | 230 | 7.70
| K-100E | 20x20 | 3.83 | 230 | 7.70
| K-64S | 20x20 | 3.83 | 230 | 7.70
| K-86S | 20x20 | 3.83 | 230 | 7.70
| K-100S | 20x20 | 3.83 | 230 | 7.70
CONVEYOR DISHWASHING MACHINES
| Model | Conveyor | Flow | Usage | (Max.)
| Number | Width | gpm | gph | (ft/min.)
| B 230 VAP | 24 | 1 | 85 | 3.8
3-Track Rackless Conveyor [2]
| BA 323 P-CU3B | 29 | 5.8 | 346 | 7
Single-Track Rackless Conveyor
| BA 133 PC | 36 | 1.9 | 114 | 7
Single Tank Rackless Conveyor - Hot Water Sanitizing[3]
| B 230 VAP-N | 23.4 | 2.99 | 179 | 8.0
| B 230 VP-N | 23.4 | 2.99 | 179 | 8.0
| B-US 231 | 23.4 | 1.67 | 100 | 6.0
| B-US 231 LPW | 23.4 | 1.67 | 100 | 8.0
| B-US 231 PW | 23.4 | 1.67 | 100 | 6.0
| B-US 281 LPW | 28.5 | 2.2 | 132 | 11.0
| BA 532 PG-N | 28.5 | 3.95 | 237 | 10.0
Multiple Tank Rackless Conveyor - Hot Water Sanitizing[3]
| B 460 VAP-N | 23.4 | 2.99 | 179 | 8.2
| B 460 VP-N | 23.4 | 2.99 | 179 | 8.2
| B 690 VAP-N | 23.4 | 2.99 | 179 | 8.2
| B 690 VP-N | 23.4 | 2.99 | 179 | 8.2
| B-US 232 LPW | 23.4 | 2.01 | 121 | 10.0
| B-US 232 PW | 23.4 | 2.99 | 179 | 8.2
| B-US 233 LPW | 23.4 | 2.29 | 137 | 12.0
| B-US 233 PW | 23.4 | 2.99 | 179 | 8.2
| B-US 282 LPW | 28.5 | 2.64 | 159 | 12.0
| B-US 283 LPW | 28.5 | 3.08 | 185 | 14.0
| BA 533 PG-N | 28.5 | 3.95 | 237 | 12.0
| BA 534 PG-N | 28.5 | 3.95 | 237 | 13.6
Single Tank Rack Conveyor - Hot Water Sanitizing[4] [5]
| K-44E | 20x20 | 3.10 | 186 | 6.14
| K-44S | 20x20 | 3.10 | 186 | 6.14
| K-54E | 20x20 | 3.90 | 234 | 7.23
| K-54S | 20x20 | 3.90 | 234 | 7.23
| K-66E | 20x20 | 3.10 | 186 | 6.14
| K-66S | 20x20 | 3.10 | 186 | 6.14
| K-76E | 20x20 | 3.90 | 234 | 7.23
| K-76S | 20x20 | 3.90 | 234 | 7.23
| K-80E | 20x20 | 3.10 | 186 | 6.14
| K-80S | 20x20 | 3.10 | 186 | 6.14
| K-90E | 20x20 | 3.90 | 234 | 7.23
| K-90S | 20x20 | 3.90 | 234 | 7.23
Multiple Tank Rack Conveyor - Hot Water Sanitizing[4] [5]
| K-100E | 20x20 | 3.83 | 230 | 7.70
| K-100S | 20x20 | 3.83 | 230 | 7.70
| K-64E | 20x20 | 3.83 | 230 | 7.70
| K-64S | 20x20 | 3.83 | 230 | 7.70
| K-86E | 20x20 | 3.83 | 230 | 7.70
| K-86S | 20x20 | 3.83 | 230 | 7.70
STATIONARY RACK DISHWASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
Single Tank Door - Hot Water Sanitizing
| FV 40.2 | 20x20 | N/A | 35.6 | 81 | 9
| DV 80.2 | 20x20 | N/A | 57.3 | 41 | 10
| FV 130.2 | 27.5x33.5 | N/A | 46.1 | 147 | 12
STATIONARY RACK POT, PAN, AND UTENSIL WASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
Single Tank Stationary Rack - Hot Water Sanitizing
| FV 130.2 | 27.5x33.5 | N/A | 46.1 | 147 | 12
MOYER DIEBEL LIMITED
STATIONARY RACK DISHWASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
Single Tank, Chemical Sanitizing Undercounter Dishwasher
| 401-LT | 20x20 | N/A | 35.7 | 80 | 23
| 500T | 20x20 | 3.6 | 38 | 80 | 23
| 501-LT | 20x20 | 3.6 | 38 | 80 | 23
| 501-UTL | 20x20 | 3.6 | 38 | 80 | 23
| MD 18-1 | 16x16 | 2.0 | 60 | 50 | 23
| MD 18-2 | 16x16 | 2.0 | 60 | 50 | 23
Single Tank, Hot Water, Undercounter Dishwasher
| 301-HT | 20x20 | N/A | 14.6 | 121 | 15
| 401-HT | 20x20 | N/A | 35.7 | 80 | 23
| 401-HTN | 20x20 | N/A | 35.7 | 80 | 23
| 500-HT | 20x20 | 3.6 | 38 | 80 | 23
| 500-UT | 20x20 | 3.6 | 38 | 80 | 23
| 501-HT | 20x20 | 3.6 | 38 | 80 | 23
| 501-HTN | 20x20 | 3.6 | 38 | 80 | 23
| 501-UT | 20x20 | 3.6 | 38 | 80 | 23
Single Tank Door, Hot Water
| MH6N | 20x20 | 5.1 | 66 | 45 | 14
| MH60 | 20x20 | 5.1 | 66 | 45 | 14
| MH65 | 20x20 | N/A | 48.4 | 43 | 10
| MH70 | 20x20 | N/A | 48.4 | 43 | 10
Single Tank Door Chemical Sanitizing
| MDM-1000 | 20x20 | N/A | 82 | 45 | 13
| MH6L | 20x20 | 5.2 | 66 | 45 | 14
NATIONAL CONVEYOR CORPORATION
STATIONARY RACK POT, PAN, AND UTENSIL WASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
Single Tank Stationary Rack - Hot Water Sanitizing
| NC-880-GPW-N | 27x22 | 7.85 | 57.85 | 200 | 34
| NC-880-GPW-SA-N | 27x22 | 7.85 | 57.85 | 200 | 34
STERO CO. (THE)
CONVEYOR DISHWASHING MACHINES
| Model | Conveyor | Flow | Usage | (Max.)
| Number | Width | gpm | gph | (ft/min.)
Multiple Tank Conveyor (Tray Washer), Hi-Temp
| STW-110 |  | 4.49 | 270 | 14.8
Multiple Tank Conveyor, Hi-Temp
| SC-1-2-7-4 | 20x20 | 4.2 | 252 | 10
| SC-1-6-3-4 | 20x20 | 4.2 | 252 | 10
| SC-1-6-7-4 | 20x20 | 4.2 | 252 | 10
| SC-2-7-4 | 20x20 | 4.2 | 252 | 10
| SC-5-2-7-4 | 20x20 | 4.2 | 252 | 10
| SC-5-6-3-4 | 20x20 | 4.2 | 252 | 10
| SC-5-6-7-4 | 20x20 | 4.2 | 252 | 10
| SC-6-3-4 | 20x20 | 4.2 | 252 | 10
| SC-6-7-4 | 20x20 | 4.2 | 252 | 10
| SCT-108S | 20x20 | 4.53 | 272 | 8.6
| SCT-108SC | 20x20 | 4.53 | 272 | 8.6
| SCT-120S | 20x20 | 5.3 | 318 | 13
| SCT-120SC | 20x20 | 5.3 | 318 | 13
| SCT-120SM | 20x20 | 5.3 | 318 | 13
| SCT-150SM | 20x20 | 5.3 | 318 | 13
| SCT-44-10-SC-1-3-4 | 20x20 | 4.92 | 295 | 7
| SCT-44-10-SC-3-4 | 20x20 | 4.92 | 295 | 7
| SCT-44-SC-1-3-4 | 20x20 | 4.92 | 295 | 7
| SCT-44-SC-3-4 | 20x20 | 4.92 | 295 | 7
| SCT-54-SC-1-3-4 | 20x20 | 4.92 | 295 | 7
| SCT-54-SC-3-4 | 20x20 | 4.92 | 295 | 7
| SCT-64 | 20x20 | 3.77 | 226 | 6.9
| SCT-76 | 20x20 | 4.53 | 272 | 8.6
| SCT-76S-SC-3-4 | 20x20 | 4.92 | 295 | 7
| SCT-86S | 20x20 | 3.77 | 226 | 6.9
| SCT-94S | 20x20 | 3.77 | 226 | 6.9
| SCT-94SC | 20x20 | 3.77 | 226 | 6.9
| SCT-94SM | 20x20 | 4.53 | 272 | 8.6
Rackless Multiple Tank Conveyor, Hi-Temp [7]
| STPC | 25 | 4.6 | 276 | 12
| STPC (Four Tank) | 25 | 3.8 | 228 | 17.3
| STPCW | 31 | 5.6 | 336 | 12
| STPCW (Four Tank) | 31 | 3.9 | 234 | 17.3
Rackless Multiple Tank Conveyor, Hi-Temp,Combination Traywasher/Dishwasher [7]
| SCBT | 29.5 | 6.8 | 408 | 10
Single Tank Conveyor Chemical Sanitizing
| SC-1-2-4-CSA | 20x20 | 4.84 | 250 | 3.8
| SC-1-2-4-CSA-LW | 20x20 | 2 | 120 | 2.3
| SC-1-6-4-CSA | 20x20 | 4.84 | 250 | 3.8
| SC-1-6-4-CSA-LW | 20x20 | 2 | 120 | 2.3
| SC-1-SCT-44-10-CSA | 20x20 | 4.84 | 250 | 4.3
| SC-1-SCT-44-CSA | 20x20 | 4.84 | 250 | 4.3
| SC-2-4-CSA | 20x20 | 4.84 | 250 | 3.8
| SC-2-4-CSA-LW | 20x20 | 2 | 120 | 2.3
| SC-5-2-4-CSA | 20x20 | 4.84 | 250 | 3.8
| SC-5-2-4-CSA-LW | 20x20 | 2 | 120 | 2.3
| SC-5-6-4-CSA | 20x20 | 4.84 | 250 | 5.9
| SC-5-6-4-CSA-LW | 20x20 | 2 | 120 | 3.5
| SC-6-4-CSA | 20x20 | 4.84 | 250 | 5.9
| SC-6-4-CSA-LW | 20x20 | 2 | 120 | 3.5
| SCT-44-10-CSA | 20x20 | 4.84 | 250 | 5.7
| SCT-44-10-CSA-LW | 20x20 | 2 | 120 | 3.5
| SCT-44-CSA | 20x20 | 4.84 | 250 | 5.7
| SCT-44-CSA-LW | 20x20 | 2 | 120 | 3.5
| SCT-66S-CSA | 20x20 | 4.84 | 250 | 5.7
| SCT-66S-CSA-LW | 20x20 | 2 | 120 | 3.5
| SCT-76S-CSA | 20x20 | 4.84 | 250 | 5.7
| SCT-76S-CSA-LW | 20x20 | 2 | 120 | 3.5
| SCT-76SC-CSA | 20x20 | 4.84 | 250 | 5.7
| SCT-76SC-CSA-LW | 20x20 | 2 | 120 | 3.5
| SCT-90S-CSA | 20x20 | 4.84 | 250 | 5.7
| SCT-90S-CSA-LW | 20x20 | 2 | 120 | 3.5
Single Tank Conveyor, Hi-Temp
| SC-1-2-4 | 20x20 | 5.02 | 301 | 3.8
| SC-1-2-4-LW | 20x20 | 2 | 120 | 2.3
| SC-1-6-4 | 20x20 | 5.02 | 301 | 5.9
| SC-1-6-4-LW | 20x20 | 2 | 120 | 3.5
| SC-2-4 | 20x20 | 5.02 | 301 | 3.8
| SC-2-4-LW | 20x20 | 2 | 120 | 2.3
| SC-5-2-4 | 20x20 | 5.02 | 301 | 3.8
| SC-5-2-4-LW | 20x20 | 2 | 120 | 2.3
| SC-5-6-4 | 20x20 | 5.02 | 301 | 5.9
| SC-5-6-4-LW | 20x20 | 2 | 120 | 3.5
| SC-6-4 | 20x20 | 5.02 | 301 | 5.9
| SC-6-4-LW | 20x20 | 2 | 120 | 3.5
| SCT-44 | 20x20 | 4.84 | 290 | 5.8
| SCT-44-10 | 20x20 | 4.84 | 290 | 5.8
| SCT-44-10-LW | 20x20 | 2 | 120 | 3.5
| SCT-44-LW | 20x20 | 2 | 120 | 3.5
| SCT-66S | 20x20 | 4.84 | 290 | 5.8
| SCT-66S-LW | 20x20 | 2 | 120 | 3.5
| SCT-76S | 20x20 | 4.84 | 290 | 5.8
| SCT-76S-LW | 20x20 | 2 | 120 | 3.5
| SCT-76SC | 20x20 | 4.84 | 290 | 5.8
| SCT-76SC-LW | 20x20 | 2 | 120 | 3.5
| SCT-90S | 20x20 | 4.84 | 290 | 5.8
| SCT-90S-LW | 20x20 | 2 | 120 | 3.5
CONVEYOR POT, PAN, AND UTENSIL WASHING MACHINES
| Model | Conveyor | Flow | Usage | (Max.)
| Number | Width | gpm | gph | (ft/min.)
Multiple Tank Conveyor - Hot Water Sanitizing
| STBUW | 27 | 7.5 | 447 | 10
STATIONARY RACK DISHWASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
Single Tank Chemical Sanitizing
| SC-20-1-AM | 20x20 |  | 98 | 40 | 20
| SC-20-2-AM | 2*20x20 |  | 196 | 40 | 20
| SC-25-1M | 20x20 |  | 98 | 40 | 20
| SC-25-2M | 2*20x20 |  | 196 | 40 | 20
| SC-25-3M | 20x20 |  | 98 | 40 | 20
Single Tank Stationary Rack, Hi-Temp
| SD-2RA | 20x20 | 6.2 | 92 | 40 | 15
| SD-2RA-HH | 20x20 | 7.8 | 72 | 40 | 10
| SDRA | 20x20 | 6.2 | 92 | 40 | 15
| U-31-A | 24x28 | 11.2 | 70 | 120 | 15
| U-31-A2 | 24x28 | 22.4 | 140 | 120 | 15
| U-31-AC | 24x28 | 11.2 | 70 | 120 | 15
STATIONARY RACK POT, PAN, AND UTENSIL WASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
Single Tank Stationary Rack - Hot Water Sanitizing
| U-31-A | 24x28 | 11.2 | 70 | 120 | 15
| U-31-A2 | 24x28 | 22.4 | 140 | 120 | 15
| U-31-AC | 24x28 | 11.2 | 70 | 120 | 15
VALU-CLEAN
STATIONARY RACK DISHWASHING MACHINES
| Model | Rack Size | Flow | Usage | (seconds)
| Number | Width | gpm | gph | Wash | Rinse
Single Tank, Chemical Sanitizing Undercounter Dishmachines
| VC 18-1 | 16x16 | 2.0 | 60 | 50 | 23
| VC 18-2 | 16x16 | 2.0 | 60 | 50 | 23
| VC41LT | 20x20 |  | 35.7 | 80 | 23
| VC51LT | 20x20 | 3.6 | 38 | 80 | 23
Single Tank Door Chemical Sanitizing Dishmachines
| VC-1000 | 20x20 | N/A | 82 | 45 | 13

## Recovery Rates
Recovery Rate (GPH) of Existing or Proposed Water Heater
Enter the input (BTU or kW) of the existing or proposed water heater
The Recovery Rate in Gallons Per Hour (GPH) will be calculated
Enter BTU (000's) of existing or proposed gas water heater: |  |  |  | ,000 BTU
Enter kW of existing or proposed electric water heater: |  |  |  | kW
Calculated Recovery Rates (GPH):
|  | Gas Water Heater | Electric Water Heater
| 100°F temperature rise: | 0 | 0
| 90°F temperature rise: | 0 | 0
| 80°F temperature rise: | 0 | 0
| 70⁰F temperature rise | 0 | 0